## Slide 1: MPC vs DRL
Updates
Yangyang Fu
7/19/2021

## Slide 2
Preliminary Case Studies
Fan Coil Unit System
Zone
DX System
Zone
Env1: Single Zone FCU system:
Control variable: air flow rate
Objective: minimize energy cost while maintaining comfort level
Env2: Single Zone DX system:
Control variable: zone air temperature cooling setpoint
Objective: minimize energy cost while maintaining comfort level

## Slide 3
MPC Formulations
MPC Formulations
 | Env 1: FCU + Single Zone | Env 2: DX + Single Zone
 | Zone supply air flowrate | Zone air temperature setpoint
 | Fan power | System total power
 | Zone air temperature | 
 | Energy price/cost | 
 | Temperature violation | 
 | Weather conditions | 
 | Lower bounds: 22oC for occupied hours, 12oC for unoccupied hours | 
 | Upper bounds: 26oC for occupied hours, 30oC for unoccupied hours | 
 | Prediction horizon; 8 steps (one step is 15-minute) Control horizon: 1 step | 
 | Env 1: FCU + Single Zone | Env 2: DX + Single Zone
 | Zone supply air flowrate | Zone air temperature setpoint
 | Fan power | System total power
 | Zone air temperature | 
 | Energy price/cost | 
 | Temperature violation | 
 | Weather conditions | 
 | Lower bounds: 22oC for occupied hours, 12oC for unoccupied hours | 
 | Upper bounds: 26oC for occupied hours, 30oC for unoccupied hours | 
 | Prediction horizon; 8 steps (one step is 15-minute) Control horizon: 1 step | 
Energy cost
Temperature violation penalty
Metric | Env 1: FCU + Single Zone |  | Env 2: DX + Single Zone | 
 | Zone Air Temperature Prediction | Power Prediction | Zone Air Temperature Prediction | Power Prediction
 | 2.4% | 16% | 2.4% | 21%
 | 0.99 | 0.99 | 0.99 | 0.97
Metric | Env 1: FCU + Single Zone |  | Env 2: DX + Single Zone | 
 | Zone Air Temperature Prediction | Power Prediction | Zone Air Temperature Prediction | Power Prediction
 | 2.4% | 16% | 2.4% | 21%
 | 0.99 | 0.99 | 0.99 | 0.97
MPC Settings

## Slide 4
DRL Formulations
State | Description
 | Time
 | Zone air temperature at
 | Outdoor air temperature at
 | Solar radiation at
 | Power at
 | Predicted outdoor air temperature at
 | Predicted outdoor air temperature at
 | Predicted outdoor air temperature at
 | Predicted solar radiation at
 | Predicted solar radiation at
 | Predicted solar radiation at
State | Description
 | Time
States Design
Learning Algorithm Settings
Reward
Energy cost
Temperature violation penalty
Same settings as MPC
Learning Algorithm – DQN
  Deep learning ANN architecture – [nStates, 50, 100, 200, 400, nActions]
  Learning rate: 0.0003
  Decay factor: 0.99
Training Settings
  Number of epochs: 50
  Control time step: 15 min

## Slide 5
Env 1: Previous Results
=0.01
=1
=100
=1000
FCU Fan Speed Control – Epochs=20

## Slide 6
Env 1: FCU Fan Speed Control – Epochs=50
=0.01
=1
=10
=100
=1000
=0.1

## Slide 7
epoch=50, =10
epoch=50, =1000

## Slide 8
Env1: Latest Results
Environment Response Study
Fan off all day, without internal heat gain
Room temperature increase to 50oC due to envelope heat transfer
Fan off all day, with internal heat gain
Room temperature increase to 55oC due to envelope heat transfer

## Slide 9
Thermal Mass
m=1
m=2
m=5

## Slide 10
Precooling Test
Case | Energy [kWh] | Cost($)
Upper bound | 17.2/1000*2 | 0.0085
precool | 79.7/1000+10/1000 | 0.0146