## Slide 1: MPC vs DRL

## Slide 2
Preliminary Case Studies
Fan Coil Unit System
Zone
DX System
Zone
Env1: Single Zone FCU system:
Control variable: air flow rate
Objective: minimize energy cost while maintaining comfort level
Env2: Single Zone DX system:
Control variable: zone air temperature cooling setpoint
Objective: minimize energy cost while maintaining comfort level

## Slide 3
MPC Formulations
MPC Formulations
 | Env 1: FCU + Single Zone | Env 2: DX + Single Zone
 | Zone supply air flowrate | Zone air temperature setpoint
 | Fan power | System total power
 | Zone air temperature | 
 | Energy price/cost | 
 | Temperature violation | 
 | Weather conditions | 
 | Lower bounds: 22oC for occupied hours, 12oC for unoccupied hours | 
 | Upper bounds: 26oC for occupied hours, 30oC for unoccupied hours | 
 | Prediction horizon; 8 steps (one step is 15-minute) Control horizon: 1 step | 
 | Env 1: FCU + Single Zone | Env 2: DX + Single Zone
 | Zone supply air flowrate | Zone air temperature setpoint
 | Fan power | System total power
 | Zone air temperature | 
 | Energy price/cost | 
 | Temperature violation | 
 | Weather conditions | 
 | Lower bounds: 22oC for occupied hours, 12oC for unoccupied hours | 
 | Upper bounds: 26oC for occupied hours, 30oC for unoccupied hours | 
 | Prediction horizon; 8 steps (one step is 15-minute) Control horizon: 1 step | 
Energy cost
Temperature violation penalty
Metric | Env 1: FCU + Single Zone |  | Env 2: DX + Single Zone | 
 | Zone Air Temperature Prediction | Power Prediction | Zone Air Temperature Prediction | Power Prediction
 | 2.4% | 16% | 2.4% | 21%
 | 0.99 | 0.99 | 0.99 | 0.97
Metric | Env 1: FCU + Single Zone |  | Env 2: DX + Single Zone | 
 | Zone Air Temperature Prediction | Power Prediction | Zone Air Temperature Prediction | Power Prediction
 | 2.4% | 16% | 2.4% | 21%
 | 0.99 | 0.99 | 0.99 | 0.97
MPC Settings
Max usuallt not used in MPC obj
Square \delta T

## Slide 4
DRL Formulations
State | Description
 | Time
 | Zone air temperature at
 | Outdoor air temperature at
 | Solar radiation at
 | Power at
 | Predicted outdoor air temperature at
 | Predicted outdoor air temperature at
 | Predicted outdoor air temperature at
 | Predicted solar radiation at
 | Predicted solar radiation at
 | Predicted solar radiation at
State | Description
 | Time
States Design
Learning Algorithm Settings
Reward
Energy cost
Temperature violation penalty
Same settings as MPC
Learning Algorithm – DQN
  Deep learning ANN architecture – [nStates, 50, 100, 200, 400, nActions]
  Learning rate: 0.0003
  Decay factor: 0.99
Training Settings
  Number of epochs: 50
  Control time step: 15 min

## Slide 5
Env 1: FCU Fan Speed Control – Epochs=20
=0.01
=1
=100
=1000

## Slide 6
Env 1: FCU Fan Speed Control – Epochs=50
=0.01
=1
=10
=100
=1000
=0.1

## Slide 7
epoch=50, =10
epoch=50, =1000

## Slide 8
Env 2: DX System Control – Epochs=20
=0.01
=1
=10
=100
=1000
=0.1

## Slide 9
Env 2: DX System Control – Epochs=50
=0.01
=1
=10
=100
=1000
=0.1

## Slide 10
epoch=50, =100
epoch=50, =1000

## Slide 11
1. Comparison Matrix:
- Reward is not the only metric
- Other control objectives should also be compared
2. Tuning DRL is time-consuming
- Multiple factors – need significant tome to figure out the impact of each parameter
3. What information we can get from “training epochs”?
- How to interpret training epochs to the number of data required for training DRL?
- How this can guide practical training
Some thoughts

## Slide 12
!!! Formulation; states?reward? Reference-tracking problem?
  DRL for linear
cost function – setpoint tracking
! - Other DRL? - Tianshou DRL package in docker: https://tianshou.readthedocs.io/en/master/index.html
Should include historical measurements in DRL states? As in MPC
  Noisy inputs might be useful
X. DRL reward – how many steps ahead
6. Compare real performance instead of only rewards
Done
. Implementaion of controls for comparison
. Objective formulation (value) might not be of interest
. Setpoints/control actions
. Energy cost,
. Tmeperature …
7. MPC is better maybe because of MPC is nosiy-free.
8. Max make the reward function nonlinear? For MPC
10. Can we get future rewards from DRL and compare??
11. DRL trianinig time – continuous states more time consuming than discrete
(1). Speed up from historical measurement?